RCx Plot & Rule Catalog Field guide for selecting the correct Streamlit view, operating gate, rule equation, and Word-report destination

| Client | [CLIENT NAME] | Facility | [FACILITY / SITE] |
| --- | --- | --- | --- |
| Report period | [START] to [END] | Project / Dataset | [SYSTEM / EQUIPMENT] |
| Prepared by | [ENGINEER] | Reviewed by | [REVIEWER] |
| Data source | [CSV / SQL / BAS EXPORT] | Revision | [REV / DATE] |

Workflow 1) Validate data and point roles. 2) Select mechanical family. 3) Apply the required operating gate. 4) tune thresholds deliberately. 5) capture Plotly evidence. 6) paste into the matching family template. 7) document verification.

# Mechanical family template map

| Family | Template | Recommended plots | Typical gates |
| --- | --- | --- | --- |
| AHU / RTU | rcx_ahu_air.docx | Supply-air-temperature control, Economizer operation, Duct-static-pressure control, Fan and coil sequencing | Controlled system enabled; Fan on; economizer enabled; Fan on; occupied or mechanical mode as applicable; Fan on; valid OAT and damper; Supply fan proven on |
| VAV / Zone | rcx_zones_vav.docx | Zone-temperature distribution, Representative VAV trend, Comfort heatmap, Terminal control scatter | Mapped zone sensors; Occupied schedule; Occupied; airflow proven; Occupied; terminal enabled; Valid time index |
| Boiler / HW plant | rcx_boiler_hw.docx | Heating-water temperature reset, Boiler staging, Pump and differential-pressure control, Plant delta-T profile | Heat demand present; Plant enabled; heating season; Pump on; Pump proven; meaningful load; Schedule available |
| Chiller / CHW / Tower | rcx_chiller_chw_tower.docx | Chilled-water temperature control, Chiller staging and loading, Condenser-water / tower performance, Pump and plant delta-T | CHW pump proven; load present; Condenser pump and tower enabled; Condenser-water flow proven; Cooling demand; Cooling plant enabled |
| Heat pump / RTU | rcx_heat_pump.docx | Unit operating sequence, Outdoor-temperature lockouts, Cycling analysis, Supply-air response | Compressor status available; Fan proven; stage active; Heating demand; Unit enabled; Valid OAT |
| Meter / Utility | rcx_metering.docx | Load profile, Daily energy and weather, Baseload and off-hours, Demand-duration curve | Daily energy and weather coverage; Demand units validated; Meter series loaded; Schedule available |
| Weather / OAT | rcx_weather.docx | BAS vs reference weather, Bias by hour and season, Weather data coverage, Operational sensitivity | Expected reporting interval; Minimum overlap and coverage; Reference series loaded; Sufficient duration; Time-aligned BAS and reference data |

# Rule documentation checklist

| Rule | Diagnostic intent | Equation / test | Run gate | Result | Engineer note |
| --- | --- | --- | --- | --- | --- |
| SV-RANGE | Detect values outside plausible engineering bounds. | x < lower_bound OR x > upper_bound | Valid timestamp; role mapped | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-FLATLINE | Detect a sensor that does not materially change. | range(x over window) <= epsilon | Minimum sample count | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-SPIKE | Detect abrupt, isolated changes. | ¦x_t - x_(t-1)¦ > max_step | Consecutive valid samples | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-STALE | Detect repeated or outdated values. | age > stale_limit OR repeated_count > limit | Expected reporting interval | [PASS / FAULT / N/A] | [INTERPRETATION] |
| EQUIPMENT RULE | State one specific detectable condition. | Show variables, inequality, persistence, and elapsed-time calculation. | State enabled/occupied/flow prerequisites. | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SKIPPED | Explain why a rule did not run. | Missing role, wrong equipment type, inadequate samples, or invalid units. | Record explicitly; do not treat as pass. | [PASS / FAULT / N/A] | [INTERPRETATION] |

# Plot capture checklist

Use a descriptive chart title with site, equipment, rule, and date range.

Show engineering units and readable legends.

Include command/status or occupancy traces needed to prove the operating gate.

Show setpoints, thresholds, and reference lines.

Use consistent axes for before/after verification.

Avoid screenshots that conceal missing data or filtered periods.

# Engineer certification and limitations

This workpaper is intended for engineering screening and retro-commissioning documentation. Results depend on point mapping, sensor quality, timestamps, operating gates, and selected thresholds. The engineer should verify findings against sequences of operation, field conditions, and control-system trends before implementation.

| Prepared by | [NAME / SIGNATURE] | Date | [DATE] |
| --- | --- | --- | --- |
| Reviewed by | [NAME / SIGNATURE] | Date | [DATE] |