Heat Pump & Packaged Unit RCx Workpaper Compressor staging, reversing mode, auxiliary heat, fan operation, lockouts, and zone response

| Client | [CLIENT NAME] | Facility | [FACILITY / SITE] |
| --- | --- | --- | --- |
| Report period | [START] to [END] | Heat pump / RTU | [SYSTEM / EQUIPMENT] |
| Prepared by | [ENGINEER] | Reviewed by | [REVIEWER] |
| Data source | [CSV / SQL / BAS EXPORT] | Revision | [REV / DATE] |

How to use this template Run the relevant Streamlit analysis, apply the intended operating filters and rule thresholds, download or capture the Plotly figures, paste each figure into the matching placeholder, and replace bracketed text with the engineer’s interpretation. Keep the rule equation and operating gate with each finding so the client can understand why the result was produced.

# Executive snapshot

| Compressor runtime | Aux heat runtime | Mode conflicts | Estimated opportunity |
| --- | --- | --- | --- |
| [000.0 h] | [000.0 h] | [000.0 h] | [$ / yr] |

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

# Data scope and readiness

DATA MODEL / POINT-MAPPING SCREENSHOT Paste the Streamlit role-mapping or equipment summary view. Include equipment count, mapped roles, missing roles, sample interval, and date coverage.

| Check | Status | Evidence | Impact | Resolution |
| --- | --- | --- | --- | --- |
| Timestamp continuity | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Engineering units | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Sensor plausibility | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Role mapping completeness | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Operating schedule | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Weather alignment | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |

# Diagnostic rule register

| Rule | Diagnostic intent | Equation / test | Run gate | Result | Engineer note |
| --- | --- | --- | --- | --- | --- |
| SV-RANGE | Detect values outside plausible engineering bounds. | x < lower_bound OR x > upper_bound | Valid timestamp; role mapped | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-FLATLINE | Detect a sensor that does not materially change. | range(x over window) <= epsilon | Minimum sample count | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-SPIKE | Detect abrupt, isolated changes. | ¦x_t - x_(t-1)¦ > max_step | Consecutive valid samples | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-STALE | Detect repeated or outdated values. | age > stale_limit OR repeated_count > limit | Expected reporting interval | [PASS / FAULT / N/A] | [INTERPRETATION] |
| HP-MODE-CONFLICT | Detect heating/cooling command conflict. | heating_command AND cooling_command | Unit enabled | [PASS / FAULT / N/A] | [INTERPRETATION] |
| HP-AUX-HEAT | Detect excessive or premature auxiliary heat. | aux_heat_on while OAT > lockout OR compressor capacity not exhausted | Heating demand | [PASS / FAULT / N/A] | [INTERPRETATION] |
| HP-SHORT-CYCLE | Detect excessive compressor starts. | starts/hour > limit OR median cycle < minimum | Compressor status available | [PASS / FAULT / N/A] | [INTERPRETATION] |
| HP-LOCKOUT | Verify compressor and heat lockout logic. | equipment_on contrary to OAT lockout threshold | Valid OAT | [PASS / FAULT / N/A] | [INTERPRETATION] |
| HP-NO-RESPONSE | Detect inadequate zone or SAT response. | commanded stage AND response slope below minimum | Fan proven; stage active | [PASS / FAULT / N/A] | [INTERPRETATION] |

# Plots and engineering interpretation

## 1. Unit operating sequence

PASTE PLOTLY FIGURE HERE Insert screenshot: zone temp, setpoints, compressor stages, fan, reversing valve, auxiliary heat.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 2. Outdoor-temperature lockouts

PASTE PLOTLY FIGURE HERE Insert screenshot: OAT with compressor and auxiliary heat status, lockout thresholds.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 3. Cycling analysis

PASTE PLOTLY FIGURE HERE Insert screenshot: starts, runtime per cycle, temperature response, occupancy.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 4. Supply-air response

PASTE PLOTLY FIGURE HERE Insert screenshot: SAT, zone temp, fan status, stage commands, mode.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

# Measures and implementation plan

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

## Measurement & verification plan

POST-IMPLEMENTATION VERIFICATION PLOT Paste the same Plotly view after implementation. Use matching axes and filters to demonstrate improvement.

# Engineer certification and limitations

This workpaper is intended for engineering screening and retro-commissioning documentation. Results depend on point mapping, sensor quality, timestamps, operating gates, and selected thresholds. The engineer should verify findings against sequences of operation, field conditions, and control-system trends before implementation.

| Prepared by | [NAME / SIGNATURE] | Date | [DATE] |
| --- | --- | --- | --- |
| Reviewed by | [NAME / SIGNATURE] | Date | [DATE] |