Weather & Outdoor-Air Sensor RCx Workpaper BAS outdoor-air sensor validation, web-weather comparison, and weather-normalized operations

| Client | [CLIENT NAME] | Facility | [FACILITY / SITE] |
| --- | --- | --- | --- |
| Report period | [START] to [END] | Weather / OAT | [SYSTEM / EQUIPMENT] |
| Prepared by | [ENGINEER] | Reviewed by | [REVIEWER] |
| Data source | [CSV / SQL / BAS EXPORT] | Revision | [REV / DATE] |

How to use this template Run the relevant Streamlit analysis, apply the intended operating filters and rule thresholds, download or capture the Plotly figures, paste each figure into the matching placeholder, and replace bracketed text with the engineer’s interpretation. Keep the rule equation and operating gate with each finding so the client can understand why the result was produced.

# Executive snapshot

| Mean OAT bias | Max deviation | Fault hours | Coverage |
| --- | --- | --- | --- |
| [0.0°F] | [0.0°F] | [000.0 h] | [00.0%] |

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

# Data scope and readiness

DATA MODEL / POINT-MAPPING SCREENSHOT Paste the Streamlit role-mapping or equipment summary view. Include equipment count, mapped roles, missing roles, sample interval, and date coverage.

| Check | Status | Evidence | Impact | Resolution |
| --- | --- | --- | --- | --- |
| Timestamp continuity | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Engineering units | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Sensor plausibility | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Role mapping completeness | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Operating schedule | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Weather alignment | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |

# Diagnostic rule register

| Rule | Diagnostic intent | Equation / test | Run gate | Result | Engineer note |
| --- | --- | --- | --- | --- | --- |
| SV-RANGE | Detect values outside plausible engineering bounds. | x < lower_bound OR x > upper_bound | Valid timestamp; role mapped | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-FLATLINE | Detect a sensor that does not materially change. | range(x over window) <= epsilon | Minimum sample count | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-SPIKE | Detect abrupt, isolated changes. | ¦x_t - x_(t-1)¦ > max_step | Consecutive valid samples | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-STALE | Detect repeated or outdated values. | age > stale_limit OR repeated_count > limit | Expected reporting interval | [PASS / FAULT / N/A] | [INTERPRETATION] |
| OAT-METEO | Compare BAS OAT to external reference weather. | ¦OAT_BAS - OAT_REF¦ > allowable_bias | Time-aligned BAS and reference data | [PASS / FAULT / N/A] | [INTERPRETATION] |
| WEATHER-GAP | Detect missing reference-weather intervals. | timestamp_gap > expected_interval | Reference series loaded | [PASS / FAULT / N/A] | [INTERPRETATION] |
| OAT-BIAS | Estimate persistent BAS outdoor-air bias. | mean(OAT_BAS - OAT_REF) over valid overlap | Minimum overlap and coverage | [PASS / FAULT / N/A] | [INTERPRETATION] |
| OAT-DRIFT | Detect changing bias over time. | slope(difference) or rolling-bias shift > limit | Sufficient duration | [PASS / FAULT / N/A] | [INTERPRETATION] |

# Plots and engineering interpretation

## 1. BAS vs reference weather

PASTE PLOTLY FIGURE HERE Insert screenshot: BAS OAT and reference OAT with difference band.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 2. Bias by hour and season

PASTE PLOTLY FIGURE HERE Insert screenshot: OAT bias heatmap or box plot by hour/month.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 3. Weather data coverage

PASTE PLOTLY FIGURE HERE Insert screenshot: missing intervals, station/source metadata, overlap period.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 4. Operational sensitivity

PASTE PLOTLY FIGURE HERE Insert screenshot: economizer or plant operation against validated OAT.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

# Measures and implementation plan

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

## Measurement & verification plan

POST-IMPLEMENTATION VERIFICATION PLOT Paste the same Plotly view after implementation. Use matching axes and filters to demonstrate improvement.

# Engineer certification and limitations

This workpaper is intended for engineering screening and retro-commissioning documentation. Results depend on point mapping, sensor quality, timestamps, operating gates, and selected thresholds. The engineer should verify findings against sequences of operation, field conditions, and control-system trends before implementation.

| Prepared by | [NAME / SIGNATURE] | Date | [DATE] |
| --- | --- | --- | --- |
| Reviewed by | [NAME / SIGNATURE] | Date | [DATE] |