Zones & VAV RCx Workpaper Zone comfort, terminal airflow, reheat, damper position, setpoint, and occupancy analysis

| Client | [CLIENT NAME] | Facility | [FACILITY / SITE] |
| --- | --- | --- | --- |
| Report period | [START] to [END] | VAV / Zone | [SYSTEM / EQUIPMENT] |
| Prepared by | [ENGINEER] | Reviewed by | [REVIEWER] |
| Data source | [CSV / SQL / BAS EXPORT] | Revision | [REV / DATE] |

How to use this template Run the relevant Streamlit analysis, apply the intended operating filters and rule thresholds, download or capture the Plotly figures, paste each figure into the matching placeholder, and replace bracketed text with the engineer’s interpretation. Keep the rule equation and operating gate with each finding so the client can understand why the result was produced.

# Executive snapshot

| Zones analyzed | Comfort compliance | Simultaneous heat/cool | Outlier zones |
| --- | --- | --- | --- |
| [000] | [00.0%] | [000.0 h] | [00] |

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

# Data scope and readiness

DATA MODEL / POINT-MAPPING SCREENSHOT Paste the Streamlit role-mapping or equipment summary view. Include equipment count, mapped roles, missing roles, sample interval, and date coverage.

| Check | Status | Evidence | Impact | Resolution |
| --- | --- | --- | --- | --- |
| Timestamp continuity | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Engineering units | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Sensor plausibility | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Role mapping completeness | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Operating schedule | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |
| Weather alignment | [OK / ISSUE] | [Metric or note] | [Rules affected] | [Action] |

# Diagnostic rule register

| Rule | Diagnostic intent | Equation / test | Run gate | Result | Engineer note |
| --- | --- | --- | --- | --- | --- |
| SV-RANGE | Detect values outside plausible engineering bounds. | x < lower_bound OR x > upper_bound | Valid timestamp; role mapped | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-FLATLINE | Detect a sensor that does not materially change. | range(x over window) <= epsilon | Minimum sample count | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-SPIKE | Detect abrupt, isolated changes. | ¦x_t - x_(t-1)¦ > max_step | Consecutive valid samples | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SV-STALE | Detect repeated or outdated values. | age > stale_limit OR repeated_count > limit | Expected reporting interval | [PASS / FAULT / N/A] | [INTERPRETATION] |
| VAV-1 | Detect terminal control deviation under occupied operation. | ¦zone_temp - active_setpoint¦ > deadband for persistence | Occupied; terminal enabled | [PASS / FAULT / N/A] | [INTERPRETATION] |
| AVG-ZONE-TEMP | Track aggregate zone temperature. | mean(valid zone temperatures) | Mapped zone sensors | [PASS / FAULT / N/A] | [INTERPRETATION] |
| ZONE-COMFORT-PCT | Measure occupied comfort compliance. | 100 × compliant occupied samples / occupied samples | Occupied schedule | [PASS / FAULT / N/A] | [INTERPRETATION] |
| FAULT-ELAPSED-HOURS | Convert fault samples to elapsed duration. | Σ sample_interval where fault = true | Valid time index | [PASS / FAULT / N/A] | [INTERPRETATION] |
| SIMULTANEOUS-HC | Screen simultaneous cooling and reheat. | cooling_demand AND reheat > threshold | Occupied; airflow proven | [PASS / FAULT / N/A] | [INTERPRETATION] |

# Plots and engineering interpretation

## 1. Zone-temperature distribution

PASTE PLOTLY FIGURE HERE Insert Plotly screenshot: zone temperature distribution, 72°F reference, occupied filters, outlier labels.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 2. Representative VAV trend

PASTE PLOTLY FIGURE HERE Insert screenshot: zone temp, heating/cooling setpoints, airflow, airflow setpoint, damper, reheat valve.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 3. Comfort heatmap

PASTE PLOTLY FIGURE HERE Insert screenshot: equipment vs time heatmap for occupied comfort deviations.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

## 4. Terminal control scatter

PASTE PLOTLY FIGURE HERE Insert screenshot: airflow error vs damper position, colored by reheat or zone deviation.

| Observed behavior | [Describe the pattern, timing, magnitude, and affected equipment.] |
| --- | --- |
| Rule evidence | [Rule ID, threshold, fault hours, percent of enabled/occupied time, and confidence.] |
| Likely causes | [Controls sequence, sensor, actuator, hydronic/airside condition, scheduling, or load.] |
| Recommended verification | [Trend additional points, field test, calibration, sequence change, or balancing.] |

# Measures and implementation plan

| Priority | Finding | Evidence | Operational impact | Recommendation | Owner / status |
| --- | --- | --- | --- | --- | --- |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |
| [H/M/L] | [Finding title] | [Plot / rule / hours] | [Comfort / energy / reliability] | [Action and verification] | [Owner / open] |

## Measurement & verification plan

POST-IMPLEMENTATION VERIFICATION PLOT Paste the same Plotly view after implementation. Use matching axes and filters to demonstrate improvement.

# Engineer certification and limitations

This workpaper is intended for engineering screening and retro-commissioning documentation. Results depend on point mapping, sensor quality, timestamps, operating gates, and selected thresholds. The engineer should verify findings against sequences of operation, field conditions, and control-system trends before implementation.

| Prepared by | [NAME / SIGNATURE] | Date | [DATE] |
| --- | --- | --- | --- |
| Reviewed by | [NAME / SIGNATURE] | Date | [DATE] |