## Cover
WattLab Engineering Notebook
ECM package screening (ESCO bin-method vs EnergyPlus)
Building | BUILDING
Package id | controls_first
Package | 1 · Controls-first (no capital RCx)
Honesty | screening — schedules / sensors / standby+DCV
Generated (UTC) | 2026-07-25T19:56:47Z
Catalog package | no-capital-rcx
n_measures | 7
Guardrail verdict | INVESTIGATE
ESCO docs | https://github.com/bbartling/py-bacnet-stacks-playground/blob/develop/vibe_code_apps_20/docs/ESCO_SPREADSHEET_CALCS.md
Note | Yellow cells on Inputs are engineer-editable. ESCO_Calcs / Compare / ROI use formulas where marked.

## Inputs
parameter | value | unit | notes
area_ft2 | 50000 | ft² | Conditioned floor area
cooling_tons |  | tons | Optional nameplate
fan_hp |  | HP | Optional supply fan
elec_rate | 0.12 | $/kWh | Blended electric rate
gas_rate | 0.8 | $/therm | Blended gas rate
discount | 0.05 | fraction | NPV discount rate
escalation | 0.02 | fraction | Utility escalation
life_years | 15 | yr | Measure life
usd_per_ft2 | 3 | $/ft² | Fallback package cost intensity
coverage | 1 | 0–1 | Fraction of floor area receiving ECMs

## ESCO_Calcs
measure_id | savings_kwh | savings_therms | calculators | annual_cost_saved_formula | notes
ECM-AHU-SCHED-ALIGN | 277595.8 | 5845.4 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-OA-DAMPER-REPAIR | 0 | 0 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-SENSOR-CRITICAL-REFRESH | 0 | 0 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-OCC-STANDBY-DCV | 46111.2 | 5042.8 | oad_unoccupied_closed,dcv_bins |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-CHILLER-LOCKOUT | 34524.9 | 0 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-SENSOR-CALIBRATION | 0 | 0 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins
ECM-RCX-SETPOINT-REVIEW | 277595.8 | 5845.4 |  |  | Screening proxy from wattlab.studio.proxies / bench ESCO bins

## EPlus_Results
measure_id | kwh_saved | therms_saved | peak_kw_delta | source
ECM-AHU-SCHED-ALIGN |  |  |  | E+ not run — ESCO only
ECM-OA-DAMPER-REPAIR |  |  |  | E+ not run — ESCO only
ECM-SENSOR-CRITICAL-REFRESH |  |  |  | E+ not run — ESCO only
ECM-OCC-STANDBY-DCV |  |  |  | E+ not run — ESCO only
ECM-CHILLER-LOCKOUT |  |  |  | E+ not run — ESCO only
ECM-SENSOR-CALIBRATION |  |  |  | E+ not run — ESCO only
ECM-RCX-SETPOINT-REVIEW |  |  |  | E+ not run — ESCO only

## Compare
measure_id | esco_kwh | ep_kwh | delta_kwh | ratio_ep_esco | esco_therms | ep_therms | verdict | light
ECM-AHU-SCHED-ALIGN | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-OA-DAMPER-REPAIR | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-SENSOR-CRITICAL-REFRESH | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-OCC-STANDBY-DCV | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-CHILLER-LOCKOUT | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-SENSOR-CALIBRATION | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW
ECM-RCX-SETPOINT-REVIEW | [6 empty] | INSUFFICIENT_EVIDENCE | YELLOW

## ROI_Capital
measure_id | implementation_cost_usd | kwh_saved | therms_saved | annual_cost_saved_usd | simple_payback_years | npv_usd | cost_formula
ECM-AHU-SCHED-ALIGN | 150000 | 277595.8 | 5845.4 |  |  | 296501.59
ECM-OA-DAMPER-REPAIR | 150000 | 0 | 0 |  |  | -150000
ECM-SENSOR-CRITICAL-REFRESH | 150000 | 0 | 0 |  |  | -150000
ECM-OCC-STANDBY-DCV | 150000 | 46111.2 | 5042.8 |  |  | -37544.43
ECM-CHILLER-LOCKOUT | 150000 | 34524.9 | 0 |  |  | -101304.1
ECM-SENSOR-CALIBRATION | 150000 | 0 | 0 |  |  | -150000
ECM-RCX-SETPOINT-REVIEW | 150000 | 277595.8 | 5845.4 |  |  | 296501.59
TOTAL

## Guardrails
check | status | detail
overall_verdict | INVESTIGATE | investigate_count=6
baseline_eui_band | skipped | No site EUI provided (load bills first).
savings_fraction | skipped | No baseline consumption provided (load bills first).
measure_cost_band | investigate | ECM-AHU-SCHED-ALIGN: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).
measure_cost_band | investigate | ECM-RCX-SETPOINT-REVIEW: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).
measure_cost_band | ok | ECM-OCC-STANDBY-DCV: $3.0/building_ft2 vs 'minor_hvac_controls' band $1.5-3.5 (2017$).
measure_cost_band | investigate | ECM-CHILLER-LOCKOUT: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).
measure_cost_band | investigate | ECM-OA-DAMPER-REPAIR: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).
measure_cost_band | investigate | ECM-SENSOR-CRITICAL-REFRESH: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).
measure_cost_band | investigate | ECM-SENSOR-CALIBRATION: $3.0/building_ft2 is above the 'rcx_tuning' reference band ($0.05-0.5, 2020$, high confidence).

## Docs
Documentation & calculator map
ESCO spreadsheet calcs (human map) | https://github.com/bbartling/py-bacnet-stacks-playground/blob/develop/vibe_code_apps_20/docs/ESCO_SPREADSHEET_CALCS.md
Python bin calculators | wattlab/bench/esco.py · wattlab/studio/proxies.py
Crosscheck | wattlab/crosscheck.py (~0.5–2× = reasonable)
Finance / NPV | wattlab/finance.py
Catalog package | no-capital-rcx
Measure ids | ECM-AHU-SCHED-ALIGN, ECM-OA-DAMPER-REPAIR, ECM-SENSOR-CRITICAL-REFRESH, ECM-OCC-STANDBY-DCV, ECM-CHILLER-LOCKOUT, ECM-SENSOR-CALIBRATION, ECM-RCX-SETPOINT-REVIEW
Agent CLI | wattlab notebook build --package controls_first --out reports/notebooks/